## Sheet1
Church Building Maintenance Workbook - Mark Goodwin - Synod Property Management (mgoodwin@mnys.org)
FIRE SAFETY
| Evacuation |  |  | Fire prevention & suppression |  |  |  | Heating systems
| Emergency lighting Egress | Posted evacuation plan | Fire drills | Sprinkler system | Portable fire extinguishers | Kitchen Ansul systems | Kitchen Exhaust systems | Boiler maintenance | Boiler inspection | Fuel storage | Portable heaters
Daily | x
Weekly | [10 empty] | x
Monthly |  | x |  | x | x
Quarterly |  |  | x |  |  |  | x
Half year | [5 empty] | x |  | x
Annually |  |  |  |  | x |  |  |  | x | x
Vendors | In the boxes above supply information on the vendors to contact and the applicable maintenance period
Notes | Egress paths and emergency lighting is critical to reducing injury or death in a fire emergency. Keep egress clear at all times ensuring a clear path all the way to the street. Check lighting periodically, have an evacuation plan, and practice fire drills as needed. Note: If a school/preschool/daycare is operated on site the evacuation plan and fire drills are required. |  |  | Sprinkler systems must be maintained by a licensed professional. Portable fire extinguishers must be serviced annually by a licensed professional, they must be accessible, hung on the wall, and inspected monthly in house. Ansul systems must be inspected and recertified twice per year by a licensed professional. Kitchen exhaust systems must be cleaned and serviced each quarter by a licensed professional. Doors to boiler rooms and stairwells must be self-closing and self-latching. If all of this is not done and reported, FDNY will come for a suprise inspection. |  |  |  | Boiler maintenance can be accomplished in house by an FDNY certifier boiler operator and/or in combination with a licensed boiler professional. Boiler inspection is required annually and must be recorded and filed with the city. Fuel storage of more that 500 gallons must be registered with the city and recertified every two years. All portable heaters (electric) must be inspected periodically during heating season for proper and safe operation. No fuel burning portable heaters are allowed indoors.
BUILDING ENVELOPE AND SECURITY
| Roof |  |  | Envelope |  |  |  | Security
| Watertight roofing | Drains & scuppers | Leaders & down-spouts | Site drainage | Doors windows watertight | Basement watertight | Façade inspection Local Law 11 | Doors windows hardware maintenance | Door locks maintenance | Video cameras security systems | Key control
Daily |  | Before each rain | Before each rain | During each rain | During each rain | After each rain
Weekly | [8 empty] | x | x
Monthly | x | x | x | x | x |  |  | x
Quarterly | [10 empty] | x
Half year
Annually | [6 empty] | x |  |  |  | x
Vendors | In the boxes above supply information on the vendors to contact and the applicable maintenance period
Notes | Inspect all roofing for signs of leakage, delamination, or deterioration monthly. Inspect and clear drains, scuppers, and rain leaders monthly and before or during each rain. |  |  | Inspect watertightness of all doors and windows at least once per month during a rainstorm. Inspect the basement during or after every rainstorm. Visually inspect facade for structural tightness twice per year and once per each five years have a professional perform the inspection. |  |  |  | Inspect, adjust, and maintain door hinges, door locks, hydraulic closers, and latches weekly or monthly depending on their use. Monitor and maintain video camera systems, DVR devices, and security systems weekly or monthly or have it done by a professional. Create a key control policy, require a key deposit as needed, and periodically review. Change or rekey all exterior locks every few years.
HEALTH & SANITARY CODE
| Water supply |  |  | Waste water |  |  |  |  | Health inspection
| Backflow valve test | Hot water temp test | Water pressure test | Sump pump | Proper grease management | Grease trap cleaning | Soil line to street | Floor drains | Regular cleaning Deep cleaning | Pest control | AED Defribulater inspection
Daily |  |  |  | x | x |  |  |  | x
Weekly
Monthly |  | x | x |  |  |  |  | x |  | x | x
Quarterly | [8 empty] | x
Half year
Annually | x |  |  |  |  | x | x |  |  |  | x
Vendors | In the boxes above supply information on the vendors to contact and the applicable maintenance period
Notes | If your facility has a backflow prevention device it must be inspected annually by a licensed professional. Periodic hot water testing can help ensure sanitary conditions as well as reduce scalding injuries. Periodic water pressure testing and replacing old inefficient fixtures can help save water and reduce waste to the sewer system. |  |  | Periodic maintenance on sump pumps can reduce back-ups and flooding hazards. Improved grease control policies that help to reduce grease into the waste water system results in less clogs and less costly cleaning and repairs to the system. Consider installing a grease trap if needed. Clean grease traps at least once annually. Maintain floor drain with proper screens and periodic cleaning. |  |  |  |  | Commercial kitchens and/or kitchens that prepare or serve food to the public are subject to unannounced inspections by the health department. The facility must be clean at all times. You must maintain a pest control contract from a licensed professional and show proof of monthly service. If you have an AED on site it must be inspected monthly and certified annually by a licensed professional.
Mechanical Electrical Plumbing (MEP) maintenance
| Electrical |  |  | Elevators, Wheelchair Lifts, and escalators |  |  |  | Gas supply/Plumbing/HVAC
| Service panel(s) | Lighting | GFCI's & wall outlets | Regular maintenance | Category 1 test | Category 5 test | Un-announced inspection by the city | Gas piping inspections and Local law 152 | Check for plumbing leaks | Change filters | Clean coils
Daily |  | x |  |  |  |  | Anytime |  | x
Weekly |  |  | x
Monthly | x |  |  | x |  |  |  | x
Quarterly | [9 empty] | x
Half year
Annually |  |  |  |  | x | Once each 5 years |  | Once each 4 years |  |  | x
Vendors | In the boxes above supply information on the vendors to contact and the applicable maintenance period
Notes | Regular inspections of electric components contribute to fire prevention. Inspect all circuit breaker panels for overloaded circuits at times of high energy use. Replace lighting with LEDs to reduce energy. Test GFCI circuits periodically to ensure they work properly. Check wall outlets periodically to ensure they are not overloaded. |  |  | Local municipalities control the overall inspections and safety systems of all elevators and vertical transportation. You must hire a licensed professional to perform regular maintenance and testing and to help guide you through the process and ensure all codes and upgrades are followed. Surprise inspections, locking out the machine, and heavy fines can be levied at any time for non-compliance. |  |  |  | In-house regular inspections of all gas piping is required and Local Law 152 requires inspection once each 4 years by a licensed professional. Regular checks for plumbing leaks can help avoid costly repair later. Change filters in HVAC units as recommended by the manufacturer or once each quarter. Industrial cleaning of condenser and evaporator coils as recommended by manufacturer or at least once per year.
Note on B28: If your facility has a backflow prevention valve it must be tested and reported annually. Backflow prevention devices are an important component of our drinking water protection program and are legally mandated under the New York State Sanitary Code and the Rules of the City of New York for those businesses identified as posing a risk to the public water supply.
Note on C28: Ideal temperature is just under 120 Fahrenheit, however for small children its safer between 110 and 115 degrees Fahrenheit. In which case this can be achieved by installing a temperature regulating device at the fixture. 120 degrees Fahrenheit is the maximum safe hot water temperature that should be delivered from a fixture. Therefore hot water above 120 degrees Fahrenheit can be considered hazardous. On the other hand if you have a commercial kitchen, health code requires that you sanitize the dishes. Ideally; to make absolutely sure that your dishes are properly sanitized, cycle them through a sanitizing dishwasher or dish machine, which requires either very hot water (160 Degrees Fahrenheit) or sanitizing chemicals.
Note on D28: Ideal water pressure is between 50 and 75 PSI. If a building has low water pressure, the problem can be made worse by poorly regulated flow of volume. Older faucets, which may allow as much as five gallons per minute (gpm) water flow, can reduce pressure in the rest of the building. Replace with new 2.5 gpm faucets. High water pressure can harm pipes, connections, and appliances. It also can create water-hammer and waste massive amounts of water. Checking for high water pressure is an often overlooked maintenance item, and one that’s easy enough to perform. Install a new pressure regulator valve and a simple pressure gauge to rectify this.
Note on E3: PLEASE NOTE: FDNY maintains a database of all commercial properties regarding inspections, service, and certification of all fire prevention and suppression systems. (churches are included) They will know if these systems are not regularly being reported as inspected and maintained and they will send somebody knocking. BIG FINES!
Note on E40: Maintenance Contracts Every building owner has to have a curent contract at all times with an approved elevator maintenance company. The contract has to contain a Maintenance Control Program that follows the elevator manufacturer’s maintenance protocol. A log of all maintenance must be kept on site and accessible to the Department of Buildings on request. The building custodian must also keep the name, address, and telephone number of the maintenance company on hand.
Note on F40: Category 1 test (CAT1) No load safety test performed between January 1st and December 31st each year by a licensed and DOB approved elevator inspector to perform annual elevator and escalator tests.
Note on G40: Category 5 test (Cat 5) Performed with rated load and speed every five years from date of installation Under New York law, building owners and managers have the responsibility of hiring competent and, more importantly, licensed and approved elevator inspectors to perform annual elevator and escalator tests. In addition, building owners bear the responsibility to obtain the services of an impartial, unaffiliated third-party agency (typically an elevator consultant) to provide witnessing of the inspection. This part of the process is called Category 5 Test Witnessing. Category Test Witnessing (or sometimes just Test Witnessing), must be an additional seperate service from the testing process, employing the use of third-party agencies to witness the category 5 testing performed by elevator inspectors. Per the NYC Department of Buildings, only third-party agencies that are licensed by DOB are permitted to witness safety tests
Note on H16: Local Law 11 of 1998 Also known as the Façade Inspection Safety Program (FISP), mandates the periodic inspection (at least once each 5 years) of the exterior walls and appurtenances (such as balconies) of buildings greater than six stories in height in New York City.
Note on H40: Unannounced inspections The New York City building codes mandate inspection twice every year for all elevators operating in the five boroughs. These inspections are performed by a third-party licensed by the city’s Department of Buildings. The building owners are generally not given notice of the inspection but are required to give the inspectors access to the elevator when the inspector shows up. Failing an inspection can lead to hefty fines.
Note on I40: Local Law 152 https://www1.nyc.gov/assets/buildings/pdf/ll_152of2016_sn.pdf Beginning January 1st 2020, this law requires the periodic inspection of gas piping systems of all buildings at least once every four years. For multifamily properties, this includes exposed gas piping outside and inside the building, in boiler rooms, in all amenity and common spaces, rooftop mechanical spaces and publicly-accessible areas